## Reference
Water quality and degradation mechanisms
https://niktrd.com/condenser-tube
Mechanism | Accelerating factor | Engineering control
Pitting and crevice corrosion | Chlorides, deposits, stagnant zones and temperature | Alloy selection, deposit control, flushing and monitoring
Erosion-corrosion | High velocity, solids and poor inlet geometry | Velocity control, inlet design, cleanliness and suitable alloy
Microbiologically influenced corrosion | Stagnation, biofilm and weak biological control | Water treatment, flushing and microbiological monitoring
Galvanic corrosion | Dissimilar metals and unfavorable area ratio | Coordinate tube, tubesheet, coating and cathodic protection
Stress-corrosion cracking | Specific environment, residual stress and temperature | Grade selection, heat treatment and fabrication control
Fouling | Hardness, suspended solids, organics and poor velocity | Treatment, online/offline cleaning and flow control
Vibration and fretting | Support spacing, shell-side velocity and resonance | Vibration analysis, support design and contact-point inspection